## Sheet1
6.1 Signal volume required for type B power-generating modules
ENERGY PARK MODULE
Position | Data type | IEC address |  |  | Name |  | Status |  | Description | Value
CONTROL SIGNALS AND FEEDBACK
1 | C_DC_NA | 1 |  |  | Active power control (AGC, aFRR, mFRR) |  | On/Off |  | Active power control (AGC, aFRR, mFRR) | 10 = On, 01 = Off
2 | C_SE_NA | 6201 |  |  | P setting |  | MW |  | Active power setpoint | Pmin - Pmax, with step x
3 | C_SE_NA | 6202 |  |  | P decrease rate |  | MW/min |  | Active power decrease rate (MW/min) | MW/min (step 1 MW/min)
4 | C_SE_NA | 6203 |  |  | P raise rate |  | MW/min |  | Active power raise rate (MW/min) | MW/min (step 1 MW/min)
5 | M_SP_TA (TB) | 3001 |  |  | Active power control (AGC, aFRR, mFRR) |  | On/Off |  | Active power control (AGC, aFRR, mFRR) according to setpoint (feedback) | On = 1, Off = 0
6 | M_ME_NA | 1001 |  |  | P setting |  | MW |  | Active power setpoint (feedback) | Pmin - Pmax, with step x
7 | M_ME_NA | 1002 |  |  | P decrease rate |  | MW/min |  | Active power decrease rate (MW/min) (1 MW/min), (feedback) | MW/min
(step 1 MW/min)
8 | M_ME_NA | 1003 |  |  | P raise rate |  | MW/min |  | Active power raise rate (MW/min) (1 MW/min), (feedback) | MW/min (step 1 MW/min)
9 | M_ME_NA | 1004 |  |  | possible P |  | MW |  | Theoretically possible active power setpoint (AGC) | MW
10 | M_ME_NA | 1005 |  |  | Minimum P |  | MW |  | Theoretically possible minimum active power setpoint (AGC) | MW
Quick limitation of active power
11 | C_DC_NA | 1 |  |  | P emergency limit 80% |  | On/Off |  | Emergency limit 80% of active power | 10=On,01=Off
12 | C_DC_NA | 2 |  |  | P emergency limit 60% |  | On/Off |  | Emergency limit 60% of active power | 10=On,01=Off
13 | C_DC_NA | 3 |  |  | P emergency limit 40% |  | On/Off |  | Emergency limit 40% of active power | 10=On,01=Off
14 | C_DC_NA | 4 |  |  | P emergency limit 20% |  | On/Off |  | Emergency limit 20% of active power | 10=On,01=Off
15 | M_SP_TA (TB) | 3002 |  |  | P emergency limit 80% |  | On/Off |  | Emergency limit 80% of active power (feedback) | On=1,Off=0
16 | M_SP_TA (TB) | 3003 |  |  | P emergency limit 60% |  | On/Off |  | Emergency limit 60% of active power (feedback) | On=1,Off=0
17 | M_SP_TA (TB) | 3004 |  |  | P emergency limit 40% |  | On/Off |  | Emergency limit 40% of active power (feedback) | On=1,Off=0
18 | M_SP_TA (TB) | 3005 |  |  | P emergency limit 20% |  | On/Off |  | Emergency limit 20% of active power (feedback) | On=1,Off=0
MEASUREMENTS, INFORMATION TO OPERATOR
19 | M_ME_NA | 1006 |  |  | Energy park module P |  | MW |  | Active power measurement, net | MW
20 | M_ME_NA | 1007 |  |  | Energy park module P |  | MW |  | Active power measurement, gross | MW
21 | M_ME_NA | 1008 |  |  | Out of work P |  | MW |  | Nominal active power out of work | MW
INFORMATION FOR THE FORECASTING SYSTEM
22 | M_ME_NA | 1010 |  |  | Wind velocity |  | m/sec |  | Wind velocity | m/sec
23 | M_ME_NA | 1011 |  |  | Wind direction |  | deg |  | Wind direction | deg
24 | M_ME_NA | 1012 |  |  | Air temperature |  | C |  | Air temperature | C
25 | M_ME_NA | 1013 |  |  | Air pressure |  | mbar (hPa) |  | NOT OBLIGATORY | mbar (hPa)
26 | M_ME_NA | 1014 |  |  | Solar intensity |  | W/m2 |  | Solar intensity | W/m2
SYNCHRONOUS MODULE
Position | Data type |  | IEC address | Name |  | Status |  | Description |  |  | Value
CONTROL SIGNALS AND FEEDBACK
1 | C_DC_NA |  | 1 | Active power control (AGC, aFRR, mFRR) |  | On/Off |  | Active power control (AGC, aFRR, mFRR) |  |  | 10 = On, 01 = Off
2 | C_SE_NA |  | 6201 | P setting |  | MW |  | Active power setpoint |  |  | Pmin - Pmax, with step x
3 | M_SP_TA (TB) |  | 3001 | Active power control (AGC, aFRR, mFRR) |  | On/Off |  | Active power control according to setpoint (feedback) |  |  | On = 1, Off = 0
4 | M_ME_NA |  | 1001 | P setting |  | MW |  | Active power setpoint (feedback) |  |  | Pmin - Pmax, with step x
5 | M_ME_NA |  | 1002 | possible P |  | MW |  | Theoretically possible active power setpoint (AGC) |  |  | MW
6 | M_ME_NA |  | 1003 | Minimum P |  | MW |  | Theoretically possible minimum active power setpoint (AGC) |  |  | MW
MEASUREMENTS, INFORMATION TO OPERATOR
7 | M_ME_NA |  | 1004 | Synchronous module P |  | MW |  | Active power measurement, net |  |  | MW
8 | M_ME_NA |  | 1005 | Synchronous module P |  | MW |  | Active power measurement, gross |  |  | MW
9 | M_ME_NA |  | 1006 | Out of work P |  | MW |  | Nominal active power out of work |  |  | MW